## CLTDc
Problem Statement :
NAME OF BUILDING | CAD/CAM LAB, IIT Guwahati
FLOOR AREA: | 1276.5 | Sq. Feet
AVG. FLOOR TO ROOM HEIGHT: | 36 | Feet
DESIGN CONDITIONS:
OUTSIDE DESIGN DRY-BULB: | 89.6 | ˚F (32C)
OUTSIDE RELATIVE HUMIDITY: | 85 | %
INDOOR DESIGN DRY -BULB: | 75.2 | ˚F(24 C)
INSIDE RELATIVE HUMIDITY: | 50 | %
DAILY RANGE: | 11.52 | ˚F
MEAN OUTDOOR TEMPERATURE | 83.3 | ˚F
CFM | 5
HEAT LOAD ESTIMATION
CLTDC = [CLTD + (78 – TR) +(TM – 85)]
Walls
WALL DIRECTION | AREA (FEET SQ): | Window n Door Area | Net Area |  | Inside Design Temp: ˚F | Outdoor Temp ˚F MAX | Outdoor Temp ˚F Min | Daily Range | Mean Temp ˚F | CLTD | CLTDc | U | Q
exterior
NORTH | 3996 | 320 | 3676 |  | 75.2 | 89.06 | 77.54 | 11.52 | 83.3 | 12 | 13.1 | 0.153 | 7367.8068
SOUTH | 3996 | 256 | 3740 |  | 75.2 | 89.06 | 77.54 | 11.52 | 83.3 | 15 | 16.1 | 0.133 | 8008.462
interior
WEST | 414 |  |  |  | 75.2 | 89.06 | 77.54 | 11.52 | 83.3 |  |  | 0.133 | 446.0022
EAST | 414 |  |  |  | 75.2 | 89.06 | 77.54 | 11.52 | 83.3 |  |  | 0.133 | 446.0022
Ground | 1276.5 |  |  |  | 75.2 | 89.06 | 77.54 | 11.52 | 83.3 |  |  | 0.258 | 2667.6297
ROOF | 1276.5 |  |  |  | Explosed to Air conditioned Room | [7 empty] | 0
[12 empty] | TOTAL | 18935.9029
Windows and doors
| Total : |  |  |  | 32+ 26= 58 | 4*2 (sq feet) each
1. CONDUCTION
Double gazed 6 mm thick | U | A | N |  | CLTD | CLTDc | Q
South Facing 32 windows | 0.53 | 8 | 32 |  | 13 | 14.1 | 1913.088
North Facing 26 windows | 0.53 | 8 | 26 |  | 13 | 14.1 | 1554.384
Door glass part(12 mm single gazed) | 0.76 | 28 | 1 |  | 13 | 6 | 127.68
[6 empty] | TOTAL | 3595.152
2. RADIATION
Reflective coated ligh 6mm thick | A | N | CLF |  | SC | Max SHGF | Q
South Facing 32 windows | 8 | 32 | 0.8 |  | 0.23 | 41 | 1931.264
North Facing 26 windows | 8 | 26 | 0.86 |  | 0.23 | 43 | 1769.1232 |  | TOTAL | 7664.4112
Door glass part(refective) | 28 | 1 | 0.86 |  | 0.3 | 43 | 310.632
| A | N | U | Q |  |  | 4011.0192
DOORS Aluminium Part | 28 | 1 | 2.08 | 58.24
Appliances
| RATING(WATT) | NUMBER(N) | CLF |  | COOLING LOAD=3.4*N*RATING*CLF
Desktop System | 650 | 50 | 0.3 |  | 33150
Printer | 430 | 1 | 0.083 |  | 121.346
Modem | 10 | 2 | 1 |  | 68
| A | W/sq feet | W
Lightening | 1276.5 | 3 | 3829.5
|  |  | TOTAL= |  | 37168.846 | W = | 126745.76BTU/hr
PEOPLE
1. Sensible | No of ppl |  |  |  | SHG | CLF | Q
Moderately active work (office) | 60 |  |  |  | 250 | 0.17 | 2550
1. Latent | No of ppl |  |  |  | SHG |  | Q
Moderately active work (office) | 60 |  |  |  | 200 |  | 12000
INFILTRATION: | [12 empty] | ,
1. Sensible Heat | CFM | ΔT | No of ppl |  | Q
Educational Institute | 5 | 14.7 | 60 |  | 4762.8
2. Latent Heat | CFM | ΔW | No of ppl |  | Q
| 5 | 0.0183 | 60 |  | 26571.6
OVERALL
SECTION | SHL | LHL | Total
WALLS | 18935.9029 |  | 18935.9029
DOORS AND WINDOWS | 7664.4112 |  | 7664.4112
Electrical Appliances | 126745.76 |  | 126745.76
People | 2550 | 12000 | 14550
infiltration | 4762.8 | 26571.6 | 31334.4
Total | 160658.8741 | 38571.6 | 199230.4741
| Q total | 199230.4741
| TR | 16.63
S

## Sheet2
Problem Statement :
NAME OF BUILDING | THERMAL SCIENCE LAB, IIT Guwahati
FLOOR AREA: | 897 | Sq. Feet
AVG. FLOOR TO ROOM HEIGHT: | 36 | Feet
DESIGN CONDITIONS:
OUTSIDE DESIGN DRY-BULB: | 89.6 | ˚F (32C)
OUTSIDE RELATIVE HUMIDITY: | 85 | %
INDOOR DESIGN DRY -BULB: | 75.2 | ˚F(24 C)
INSIDE RELATIVE HUMIDITY: | 50 | %
DAILY RANGE: | 11.52 | ˚F
MEAN OUTDOOR TEMPERATURE | 83.3 | ˚F
HEAT LOAD ESTIMATION
CLTDC = [CLTD + (78 – TR) +(TM – 85)]
WALLS
WALL DIRECTION | AREA (FEET SQ): | Window n Door Area | Net Area | Inside Design Temp: ˚F | Outdoor Temp ˚F MAX | Outdoor Temp ˚F Min | Daily Range | Mean Temp ˚F | CLTD | CLTDc | U | Q
exterior
NORTH | 2808 | 216 | 2592 | 75.2 | 89.06 | 77.54 | 11.52 | 83.3 | 12 | 13.1 | 0.142 | 4821.6384
SOUTH | 2808 | 120 | 2688 | 75.2 | 89.06 | 77.54 | 11.52 | 83.3 | 13 | 14.1 | 0.133 | 5040.8064
interior
WEST | 414 |  |  | 75.2 | 89.06 | 77.54 | 11.52 | 83.3 |  |  | 0.133 | 446.0022
EAST | 414 |  |  | 75.2 | 89.06 | 77.54 | 11.52 | 83.3 |  |  | 0.133 | 446.0022
ROOF | 897 |  |  | 75.2 | 89.06 | 77.54 | 11.52 | 83.3 | 43 | 44.1 | 0.151 | 5973.2127
Ground | 897 |  |  | Explosed to Air conditioned Room | [7 empty] | 0
[11 empty] | Total= | 16727.6619
WINDOWS AND DOORS | Total : |  |  | 32+ 26= 58 | 4*2 (sq feet) each
1. CONDUCTION
Double gazed 6 mm thick | U | A | N | CLTD | CLTDc | Q
South Facing 20 windows | 0.53 | 8 | 20 | 13 | 14.1 | 1195.68
North Facing 15 windows | 0.53 | 8 | 15 | 13 | 14.1 | 896.76
Door glass part(12 mm single gazed) | 0.76 | 28 | 1 | 13 | 6 | 127.68
[6 empty] | 2220.12 |  |  |  | Total= | 6947.512
2. RADIATION
Heat Absorbing dark 6mm thick | A | N | CLF | SC | Max SHGF | Q
South Facing 20 windows | 8 | 20 | 0.8 | 0.45 | 41 | 2361.6
North Facing 15 windows | 8 | 15 | 0.86 | 0.45 | 43 | 1996.92
Door glass part(refective) | 28 | 1 | 0.86 | 0.3 | 43 | 310.632
4669.152
| A | N | U | Q
DOORS Aluminium Part | 28 | 1 | 2.08 | 58.24
PEOPLE
1. Sensible | No of ppl | SHG | CLF | Q
light work, standing | 30 | 250 | 0.17 | 1275
1. Latent | No of ppl | SHG |  | Q
light work, standing | 30 | 200 |  | 6000
ELETRICAL APPLIANCE:
|  | RATING(WATT) | NUMBER(N) | CLF | COOLING LOAD=3.4*N*RATING*CLF
Desktop System |  | 750 | 10 | 0.67 | 17085
Printer |  | 430 | 2 | 0.083 | 242.692
Modem |  | 10 | 3 | 1 | 102
Fan |  | 50 | 2 | 0.3 | 102
Refrigerator |  | 800 | 1 | 1 | 2720
Tubular Heat Exchanger |  | 2100 | 1 | 0.1 | 714
Boiling Heat Transfer |  | 500 | 1 | 0.1 | 170
Heat Conduction Unit |  | 300 | 1 | 0.1 | 102
Cooling Tower + PC data |  | 2200 | 1 | 0.1 | 748
Refrigeration System |  | 600 | 1 | 0.1 | 204
| A | W/sq feet | W | CLF |  |  |  |  | TOTAL= | 8430.266 | W= | 28747.22 | BTU/hr
Lightening | 897 | 2 | 1794 | 0.45 | 3568.266
INFILTRATION:
1. Sensible Heat | CFM | n |  | ΔT | Q
Educational Institute | 5 | 30 |  | 14.7 | 2381.4
2. Latent Heat | CFM |  |  | ΔW | Q
| 5 | 30 |  | 0.0183 | 13285.8
OVERALL
SECTION | SHL | LHL | Total
WALLS | 16727.6619 |  | 16727.6619
DOORS AND WINDOWS | 6947.512 |  | 6947.512
Electrical Appliances | 28747.22 |  | 28747.22
People | 1275 | 6000 | 7275
infiltration | 2381.4 | 13285.8 | 15667.2
Total | 56078.7939 | 19285.8 | 75364.5939
Q total | 75364.5939
TR | 16.63